| PCM Specifications For 8S /25.6V LiFePO4 Battery Pack |
| --- |
| Model: RC-8S2005-BMS |
| No. | Test item | Criterion |
| 1 | Voltage | Charging voltage | DC:28.8 V 3.6V/Cell |
|  |  | Balance voltage for single cell | 3.60+0.025V |
| 2 | Current | Balance current for single cell | 60+5mA |
|  |  | Current consumption for single cell | ≤20μA |
|  |  | Maximal continuous Charging current | 5A |
|  |  | Maximal continuous Discharging current | 20A |
| 3 | Over charge Protection | Over charge detection voltage | 3.90+0.025V |
|  |  | Over charge detection delay time | 0.5—2S |
|  |  | Over charge release voltage | 3.80+0.05V |
| 4 | Over discharge protection | Over discharge detection voltage | 2.00+0.05V |
|  |  | Over discharge detection delay time | 10-300mS |
|  |  | Over discharge release voltage | 2.3+0.05V |
| 5 | Over current protection | Over current detection voltage | 0.62v |
|  |  | Over current detection current | 100+20A |
|  |  | Detection delay time | 5ms—20mS |
|  |  | Release condition | Cut load, Automatic Recovery |
| 6 | Short protection | Detection condition | Exterior short circuit |
|  |  | Detection delay time | 200-500us |
|  |  | Release condition | Cut load, Automatic Recovery |
| 7 | Resistance | Protection circuitry (MOSFET) | ≤30mΩ |
| 8 | Temperature | Operating Temperature Range | -40~+85°C |
|  |  | Storage Temperature Range | -40~+125°C |
| 9 | Size |  | L80*W60*T13mm |